## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees on within 2 days.
Common Causes & Solutions for Compressed Air Pressure Drop
Tom Taranto, Data Power Services
Keynote Speaker
Sponsored by

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 5
Introduction
Compressed Air Best Practices® Magazine
Common Causes & Solutions for Compressed Air Pressure Drop
Sponsored by

## Slide 6: About the Speaker
Owner, Data Power Services
Over 45 years of experience in the compressed air industry
U.S. DOE Energy Expert, Compressed Air Challenge technical committee member, Compressed Air Challenge qualified instructor and instructor for Qualified AIRMaster+ Specialist Training
Sponsored by
Tom Taranto
Data Power Services

## Slide 7: Root cause of pressure loss? Friction – resistance to fluid flow
Friction loss occurs as a fluid flows through a conduit.
  Piping
  Valves
  Pipe fittings elbow, tees, reducers
  Hoses & hose fittings
  Every element that compressed air flows through in the system causes pressure loss.
Pipe resistance coefficient K
  Darcy Equation
Friction Loss
Darcy-Weisbach Equation
Notes: More information available recording Best Practices 2020 online event Sept 22nd & 23rd

## Slide 8: Pressure Loss −vs− Pipe Length
Pressure Loss is directly proportional to the pipe length.
What about pipe fittings & valves?
  Equivalent Length L/D method*
    90O elbow L/D = 30
    90O long radius elbow L/D = 16
    2” Sched 40 I.D. = 2.067” = 0.172 ft.
    90O elbow = 5.16 ft.
    90O long radius elbow = 3.44 ft.
*Baumeister – Mark’s Standard Handbook for Mechanical Engineers, 8th ed. Table 11; p 3-58.
Crane Technical Paper No. 410 twenty-fifth printing 1991, p A-29
Metric Version also available SI Units

## Slide 9: Equivalent Length Method for piping pressure loss

## Slide 10: Equivalent Length Method for piping pressure loss
Notes: Handouts include velocity charts and a handout from the Nashville 2019 EXPO Designing Piping Systems for Low Pressure Drop

## Slide 11: Compressed Air System Operating parameters that impact pressure drop
Pipe Length (equivalent length)
Compressed Air Velocity

## Slide 12: Pressure Loss from the source to tool ≤ 10%

## Slide 13: Compressed Air System Pressure Profile

## Slide 14: Compressed Air System Operating parameters that impact pressure drop
Pipe Length (equivalent length)
Compressed Air Velocity
Compressed Air Pressure

## Slide 15: Piping restrictions and Pressure drop
Pipe Length (equivalent length)
  Long pipe runs
  Long hoses
  Fittings, elbow, tee, valve
Restrictions
  Filters
  Quick Couplers
  Undersize connectors
  Abandoned Equipment

## Slide 16: Excessive length of undersize hose
Average P5 is 10 sec. data interval
Sample Rate 25 samples / sec.
Minimum P5 is minimum reading during the interval
Notes: Average readings are scan rate 25 s/sec average data interval 10 sec / data point

## Slide 17: Printed circuit board drills & routers

## Slide 18: Hose & pipe length
Transit bus manufacturer
  Enough hose to go all the way around a bus and ½ way again.
100 ft hose reel under the work bench, the work area 25 ft across.
50 ft hose reel from the 17 ft high ceiling with 4 QD fittings connected to a torque gun.

## Slide 19: Hose

## Slide 20: More hose Air hose safety
Flow
Hose
Pipe
Velocity Check or Whip Check

## Slide 21: More hose Air hose safety
Flow
Hose
Pipe
Velocity Check or Whip Check
Ball Vent Coupling

## Slide 22: Hose connection

## Slide 23: Abandoned Main Line Compressed Air Filter

## Slide 24: Abandoned Orifice Plate Flow Meter
10” diameter header with 13,800 cfm average air flow rate
Abandoned Flow Meter, 3 psid = 619,000 kWh / yr $43,330 / yr @ 0.07 / kWh
Notes: 619,000 kWh / yr @ 7 cents / kWh = $43,000 / year

## Slide 25: High Velocity and Pressure Loss
Increasing air flow
  Adding new air demands
  Installing added compressor capacity
  Leakage and compressed air waste
  High volume intermittent peak air demand
Improper size components
  FRL’s not sized for the end use air demand. Instead selected base on what’s available in the store room
  Size based on average air flow rating rather than peak air flow

## Slide 26: Compressed Air Velocity
Pressure loss
= 8.34

## Slide 27: Increased air demand & compressor capacity. Pipe Size ???
Air Demand
  700 cfm of flow @ 80 psig
  2” diameter pipe
  1000 ft long (equivalent length)
Pipe Capacity
  w/ 90 psig Initial Pressure
  362 cfm of flow @ 80 psig
  700 cfm of flow @ 53 psig

## Slide 28: Increased air demand & compressor capacity. ↑ Pressure ↑
Air Demand
  700 cfm of flow @ 80 psig
  2” diameter pipe
  1000 ft long (equivalent length)
Pipe Capacity
  Requires 120 psig Initial Pressure
  30 psig increase from 90 psig target
  724 cfm of flow @ 80 psig
~ 15% increased compressor kW
Distribution & Point of Use Pressure Drop????

## Slide 29: 700 cfm with 1000 ft of pipe – Increase Pipe Size
Air Demand
  700 cfm of flow @ 80 psig
  ??” diameter pipe 3” or 4”
  1000 ft long (equivalent length)
Pipe Capacity
  90 psig Initial Pressure (original target)
  3” Sch 40 5.5 psid branches, drop, POU
  4” Sch 40 9.0 psid branches, drop, POU
~ 0% increased compressor kW
Distribution & POU Pressure Drop is Included

## Slide 30: 700 cfm with 1000 ft of pipe – Optimize Pipe Size & Pressure
Air Demand
  700 cfm of flow @ 80 psig
  3” diameter pipe
  1000 ft long (equivalent length)
Pipe Capacity
  85 psig Initial Pressure (< original target)
  3” Sch 40 decrease pressure by 5.0 psig
~ 2.5% decreased compressor kW
Distribution & Point of Use Pressure Drop????

## Slide 31: Compressed Air Velocity
Pressure loss
= 8.34

## Slide 32: High Velocity = large pressure drop & pressure fluctuations
Pipeline pressure gradient measurement
High pipeline velocity results in:
  High pressure gradient - high velocity
  18 psig pressure loss at the greatest flow rate 3,800 cfm
  11 psig pressure loss at the lowest flow rate 2,250 cfm
  Distribution piping is not tracking with supply pressure
  Inverse mirror image of air flow rate and distribution piping pressure
Notes: There is localized pressure loss. When air flow rate peaks, supply pressure decays by about 2 psi but the downward pressure excursion of distribution pressure is about 8 psig.
Sometimes there is a localized choke point in the distribution piping that can be corrected. Other times the air flow rate is just too high for the pipeline capacity.
With system wide pressure decay there is drawdown of both supply side and distribution piping pressure.

## Slide 33: Localized Peak Air Demand

## Slide 34: Localized Peak Air Demand – Secondary Storage w/ Refill Control
1,600 cfm
peak flow
~ 900 cfm
average flow

## Slide 35: Lessons Learned
Excessively long hose
Poor connections
  Undersize components FRLs
  Unnecessary quick disconnects
Filters
  Excessive or redundant over-filtration
  Dirty filter elements, change regularly
Abandoned Equipment
Increasing compressed air demand
Increasing compressor capacity
Excessive leakage and waste
Size for peak flow (compressor sized for avg)
Reduce pipe velocity with secondary storage
Restriction to flow (Equivalent Length)
High Velocity (Constant or Peak)

## Slide 36: About the Speaker
Sponsored by
Scott Folsom
FS-Curtis
Director of Channel Development, FS-Curtis
Responsible for large rotary sales and compressed air system assessments
Compressed Air Industry since 1993, 10 Year with FS-Curtis

## Slide 37: The “System Approach” to maximizing compressed air system efficiency
Thursday March 25, 2021

## Slide 38: The “system Approach” to maximizing compressed air system efficiency
How can I maximize production efficiency?
How can I reduce scrap rate?
Is my plant operating at peak efficiency?
Is my “cost per widget” as low as it can possibly be?
What type of improvements will give me the greatest return?
Have you ever asked yourself…
If you have, then you’ve likely discovered that your compressed air system provides ample opportunity for energy efficiency improvements!
Do I need a new air compressor?
Reciprocating, Rotary Screw, or
Centrifugal?
Fixed speed or Variable speed?
Single stage or two stage?
Oil flooded or Oil free?
Does my air treatment equipment provide the air quality I need?
IS THERE ANYTHING ELSE I SHOULD BE CONSIDERING?

## Slide 39: The “system Approach” to maximizing compressed air system efficiency
Your previous questions are all valid and will need to be answered…
These questions only address concerns about the SUPPLY SIDE of your compressed air system!
What about the DEMAND SIDE?

## Slide 40: What is the supply side?
A typical compressed air system is made up of two major subsystems each containing various components.
SUPPLY SIDE & DEMAND SIDE.
Moisture separator
Condensate Drains
Oil/Water separator
Flow Controller
Bypass valves

## Slide 41: What is the Demand Side?
A typical compressed air system is made up of two major subsystems each containing various components.
SUPPLY SIDE & DEMAND SIDE.

## Slide 42: Components of demand

## Slide 43: Components of demand
In a typical plant, demand for compressed air is a lot more than just what’s required to “do the work” (cylinders, rotary actuators, etc).
There are several “components of demand” that don’t produce any “work”…they’re completely unproductive and only waste energy!
Eliminating/minimizing these wasteful components of demand will save energy…and $$.
Typical components of demand
1. INAPPROPRIATE USES: any application that can be done more effectively and/or more efficiently by a method other than compressed air.
2. LEAKS: an unintended loss of compressed air to ambient conditions.
3. ARTIFICIAL DEMAND: increased demand due to excessive system pressure.

## Slide 44: Inappropriate uses
Any application that can be done more effectively and/or more efficiently by a method other than compressed air.
Inappropriate uses
OPEN BLOWING
  Processes such as cooling, bearing cooling, drying, clean up, or clearing jams on a conveyor.
  Use a fan or low-pressure blower for general cooling, foot valves for air “shut off”, and a broom for clean up!
SPARGING
  Aerating, agitating, oxygenating, or percolating liquid with compressed air.
  Low pressure blowers are perfect for this!
DILUTE PHASE TRANSPORT
  Used in transporting solids such as powdery material in a diluted format with compressed air.
  Low pressure blower!
VACUUM VENTURI’s
  Compressed air is forced through an engineered nozzle that causes an increase in air velocity and an associated decrease in pressure, to below atmospheric (vacuum).
  Use a dedicated vacuum pump instead!
PERSONAL COOLING
  Production employees direct compressed air upon themselves to provide ventilation.
  Use a fan!

## Slide 45: Compressed air vs other energy sources
Compressed air is a necessary part of most plant operations, but it is NOT the most efficient source of energy in a plant.
Example: Powering a 1 HP air motor.
  The 1 hp air motor requires 30 acfm @ 90 psig.
  7-8 hp (5-6 kW) is required at the compressor to produce 30 acfm @ 90 psig.
  A 5 day/wk, 2 shifts/day plant that pays $.10/kW-hr, will spend $2,330/yr to produce the 30 acfm @ 90 psig required.
  A 1 hp ELECTRIC motor will cost $390/yr.
YOU DO THE MATH!

## Slide 46: leaks
An unintended loss of compressed air to ambient conditions.
Leak flow rate is a function of pressure in an uncontrolled system.
  Higher pressure = greater leak flow.
  Lower pressure = less leak flow.
Leaks happen in the compressor room, the interconnecting piping, the tanks, the joints of the plant piping system, the “dirty 30”, and the production equipment itself…
EVERY PLACE WHERE SOMETHING IS CONNECTED TO SOMETHING ELSE IS A POTENTIAL LEAK POINT.
leaks
Discharge of air through an orifice
scfm for stated orifice size in inches
psig | 1/64” | 1/32” | 1/16” | 1/8” | ¼” | 3/8”
70 | .30 | 1.20 | 4.79 | 19.2 | 77 | 173
80 | .34 | 1.34 | 5.36 | 21.4 | 86 | 193
90 | .37 | 1.48 | 5.92 | 23.8 | 95 | 213
100 | .41 | 1.62 | 6.49 | 26.0 | 104 | 234
125 | .50 | 1.98 | 7.90 | 31.6 | 126 | 284
Control waste due to leaks by minimizing the supply pressure, or…FIX THE LEAKS!
All unregulated uses will use more air when pressure increases.
A $200/yr leak cannot be felt or heard.
An $800/yr leak can be felt but not heard.
A $1,400/yr leak can be felt and heard.

## Slide 47: leaks
Leaks can be a very significant source of wasted energy in a compressed air system…upwards of 20-30% of a compressed air system’s full load output capacity can be wasted on “feeding the beast”…leaks!
With a proactive leak management campaign, leak flow rate can be reduced to 5-10% of total compressed air production capacity.
Leaks are inevitable and cannot be 100% eliminated…even a brand new piping system will have leaks regardless of what type of pipe is used.
IT’S NOT JUST ABOUT WASTED ENERGY…there are other operational losses associated with compressed air leaks.
  Leaks cause a pressure drop in the system, which can negatively affect production efficiency and product quality…leading to missed KPI metrics, and increased scrap rate.
  Leaks cause supply side equipment to “cycle” more frequently…shortening the life span…including the air compressor!
  Leaks can cause increased compressor run time, which increases maintenance requirements and expenditures.
  Leaks can lead a customer to purchase unnecessary horsepower. Fix your leaks, THEN let us come in and evaluate your system for new compressor needs.

## Slide 48: Estimating Leak Load
You can estimate leak load by observing the behavior of the pressure in the air receiver (tank).
Determine the ENTIRE system storage capacity volume (V) in cu ft. INCLUDE ALL PIPING IN THE PLANT & POINT OF USE TANKS!
Install a pressure gauge in or immediately downstream of the air receiver.
Bring the plant up to system pressure and shut off the air compressor.
Measure the time (T) it takes for the plant pressure to decay from MAX pressure (P1) to MIN pressure (P2 – usually about ½ of normal operating plant pressure), and apply some simple algebra…
Leakage (acfm) = [V x (P1-P2) / (T x 14.7)] x 1.25
V = total system storage volume in cu ft
P1 = max pressure in tank
P2 = min pressure in tank
T = time in minutes
1.25 = corrects leakage to normal system pressure…LEAKS LEAK LESS AIR AT LOWER PRESSURE!

## Slide 49: Artificial demand
Increased demand due to system pressure set higher than required to keep production equipment operating properly…excessive system pressure.
Leak flow rate is a function of pressure in an uncontrolled system.
  Higher pressure = greater leak flow.
  Lower pressure = less leak flow.
All unregulated uses will use more air when pressure increases (open blowing, blowguns, production equip w/o point of use regulator…).
Artificial demand
Discharge of air through an orifice
scfm for stated orifice size in inches
psig | 1/64” | 1/32” | 1/16” | 1/8” | ¼” | 3/8”
70 | .30 | 1.20 | 4.79 | 19.2 | 77 | 173
80 | .34 | 1.34 | 5.36 | 21.4 | 86 | 193
90 | .37 | 1.48 | 5.92 | 23.8 | 95 | 213
100 | .41 | 1.62 | 6.49 | 26.0 | 104 | 234
125 | .50 | 1.98 | 7.90 | 31.6 | 126 | 284
A 3/8” orifice will leak 284 acfm @ 125 psig.
A 3/8” orifice will leak 234 acfm @ 100 psig.
Lowering pressure by just 10 psig reduces consumption by 50 acfm…that’s a 15hp air compressor!

## Slide 50: summary
A typical compressed air system provides ample opportunity for improved efficiency.
Addressing only the supply side of the compressed air system (air compressors, dryers, filters, tanks) will not maximize the overall efficiency of the system!
Use the System Approach and analyze both the supply side and the DEMAND side for maximum efficiency improvements!
If you want to cut costs, reduce unproductive components of demand!
Wasteful components of demand (that don’t relate to production):
  Inappropriate Uses
    Explore more efficient technologies.
    Educate and eliminate inappropriate uses by plant personnel.
  Leaks
    If left unmanaged, leaks can consume up to 30% of the total compressed air capacity in a system.
  Artificial Demand
    Lower your plant pressure by controlling leaks and minimizing pressure drop.
IN SUMMARY…

## Slide 51: Thank you!

## Slide 52
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Common Causes & Solutions for Compressed Air Pressure Drop
Sponsored by

## Slide 53: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within 2 days.

## Slide 54
Thursday, April 22, 2021 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
April 2021 Webinar How to Correctly Apply & Size Oil-Free Vacuum Pumps
Andy Smiltneek
Growth Solutions Consultants
Keynote Speaker
Sponsored by